## Sheet1
| DATA(EN) | add | modbus add | byte | oder | data type | NOTE
User parameters | Mode setP | 0 | 40001 | 1 | 03 | int | 0:Cooling ;1:Heating ;2:DHW ;3:Cooling+DHW;4:Heating+DHW
| Heat SetP | 1 | 40002 | 1 | 03 | REAL | 10.0~CoolHeatMng.heat_set_max（CoolHeatMng.heat_set_max:-99~100）
| Cool SetP | 2 | 40003 | 1 | 03 | REAL | CoolHeatMng.cool_set_min~40.0（CoolHeatMng.cool_set_min:-99-100.0）
| Hotwater SetP | 3 | 40004 | 1 | 03 | REAL | 10-CoolHeatMng.heat_set_max（CoolHeatMng.heat_set_max:-99.0~100）
| hotwater_start_diff | 4 | 40005 | 1 | 03 | REAL | 1.0~15.0
| hotwater_stop_diff | 5 | 40006 | 1 | 03 | REAL | 0.0~5.0
| heat/cool start_Diff | 6 | 40007 | 1 | 03 | REAL | 1.0~15.0
| heat/cool stop_Diff | 7 | 40008 | 1 | 03 | REAL | 0.0~5.0
Engineering parameters | Heater type | 323 | 40324 | 1 | 03 | INT | 0:disalbe 1：hotwater 2：heating 3：all 4:independent
| Pump Mode | 11 | 40012 | 1 | 03 | int | 0:normal ;1:demand; 2:ineterval
| Fan Mode | 12 | 40013 | 1 | 03 | int | 0:daytime; 1:night; 2:ECO mode; 3T:presure
| E/H comp.delay | 13 | 40014 | 1 | 03 | UINT | 0-999
| Ext.temp.setp. | 14 | 40015 | 1 | 03 | real | -30.0~20.0
Status query | Unit On/OFF | 0 | 10001 | 1 | 03 | BOOL | 0:OFF 1:ON
| Inlet Temp. | 188 | 40189 | 1 | 03 | REAL | 0:OFF 2:ON
| Outlet Temp. | 189 | 40190 | 1 | 03 | REAL | 0:OFF 3:ON
| Amb.Temp. | 190 | 40191 | 1 | 03 | REAL | 0:OFF 4:ON
| Disch.gas Temp. | 191 | 40192 | 1 | 03 | REAL | 0:OFF 5:ON
| Suct.gas Temp. | 192 | 40193 | 1 | 03 | REAL | 0:OFF 6:ON
| Disch.press | 193 | 40194 | 1 | 03 | REAL | 0:OFF 7:ON
| Suct.press | 194 | 40195 | 1 | 03 | REAL | 0:OFF 8:ON
| hotwater temp | 195 | 40196 | 1 | 03 | REAL | 0:OFF 9:ON
| Coil Temp. | 196 | 40197 | 1 | 03 | REAL | 0:OFF 10:ON
| Flow switch | 1 | 10002 | 1 | 02 | BOOL | 0:OFF 11:ON
| A/C linkage switch | 3 | 10004 | 1 | 02 | BOOL | 0:OFF 12:ON
| SG_Signal | 4 | 10005 | 1 | 02 | BOOL | 0:OFF 13:ON
| EVU_Signal | 187 | 10188 | 1 | 02 | BOOL | 0:OFF 14:ON
| Outputs.DoutVal_1 | 5 | 10006 | 1 | 02 | BOOL | 0:NO 1:OFF
| Outputs.DoutVal_9 | 12 | 10013 | 1 | 02 | BOOL | 0:NO 1:OFF
| Four way valve On/OFF status | 7 | 10008 | 1 | 02 | BOOL | 0:NO 1:OFF
| Pump On/OFF status | 8 | 10009 | 1 | 02 | BOOL | 0:NO 1:OFF
| Three way valve On/OFF status | 9 | 10010 | 1 | 02 | BOOL | 0:NO 1:OFF
| Crank.heater On/OFF status | 10 | 10011 | 1 | 02 | BOOL | 0:NO 1:OFF
| chassis heater On/OFF status | 11 | 10012 | 1 | 02 | BOOL | 0:NO 1:OFF
| Fan output(%) | 197 | 40198 | 1 | 03 | REAL
| Pump out(%) | 198 | 40199 | 1 | 03 | REAL
| Fan2 RPM | 200 | 40201 | 1 | 03 | INT
| Fan1 RPM | 202 | 40203 | 1 | 03 | INT
| COMP.RPM | 205 | 40206 | 1 | 03 | REAL
| EEV1 Steps | 207 | 40208 | 1 | 03 | INT
| unit run mode | 215 | 40216 | 1 | 03 | INT | 0：Cooling 1：Heating 2：DHW
| Comp On/OFF status | 179 | 10180 | 1 | 02 | BOOL
| Fan On/OFF status | 180 | 10181 | 1 | 02 | BOOL
| GeneralMng.CurrVer.X | 325 | 40326 | 1 | 03 | INT
| GeneralMng.CurrVer.Y | 326 | 40327 | 1 | 03 | INT
| GeneralMng.CurrVer.Z | 327 | 40328 | 1 | 03 | INT
| GeneralMng.UnitType_A | 328 | 40329 | 1 | 03 | INT
| GeneralMng.UnitType_B | 329 | 40330 | 1 | 03 | INT
| BLDC_POwer | 333 | 40334 | 1 | 03 | real
| BLDC_Var | 334 | 40335 | 1 | 03 | int
| BLDC_Curret | 335 | 40336 | 1 | 03 | real
| WorkingHours.Pump | 364 | 40365 | 2 | 03 | UDINT
| WorkingHours.Comp | 366 | 40367 | 2 | 03 | UDINT
| WorkingHours.Fan | 368 | 40369 | 2 | 03 | UDINT
| WorkingHours.Three way valve | 370 | 40371 | 2 | 03 | UDINT
| Water Flow Value | 372 | 40373 | 2 | 03 | real | L/h
| Unit Power | 387 | 40388 | 2 | 03 | real | W
| Unit_COP | 389 | 40390 | 1 | 03 | real
time setting | Year | 182 | 40183 | 1 | 03 | UINT | 0~99
| Month | 183 | 40184 | 1 | 03 | UINT | 0~12
| Day | 184 | 40185 | 1 | 03 | UINT | 0~31
| Hour | 185 | 40186 | 1 | 03 | UINT | 0~23
| Minute | 186 | 40187 | 1 | 03 | UINT | 0~59
| Week | 187 | 40188 | 1 | 03 | UINT | 1~7
| timezone on/off enable | 38 | 00039 | 1 | 01 | bool
| timezone setpoing enable | 39 | 00040 | 1 | 01 | bool
| save time | 43 | 00044 | 1 | 01 | bool
Timing on/off settings | Timezone1 Mon. ON: hour | 218 | 40219 | 1 | 03 | INT | 0-23
| Timezone1 Mon. ON: minute | 219 | 40220 | 1 | 03 | INT | 0-59
| Timezone1 Tue. ON: hour | 220 | 40221 | 1 | 03 | INT | 0-23
| Timezone1 Tue. ON: minute | 221 | 40222 | 1 | 03 | INT | 0-59
| Timezone1 Wed. ON: hour | 222 | 40223 | 1 | 03 | INT | 0-23
| Timezone1 Wed. ON: minute | 223 | 40224 | 1 | 03 | INT | 0-59
| Timezone1 Thu. ON: hour | 224 | 40225 | 1 | 03 | INT | 0-23
| Timezone1 Thu. ON: minute | 225 | 40226 | 1 | 03 | INT | 0-59
| Timezone1 Fri. ON: hour | 226 | 40227 | 1 | 03 | INT | 0-23
| Timezone1 Fri. ON: minute | 227 | 40228 | 1 | 03 | INT | 0-59
| Timezone1 Sat. ON: hour | 228 | 40229 | 1 | 03 | INT | 0-23
| Timezone1 Sat. ON: minute | 229 | 40230 | 1 | 03 | INT | 0-59
| Timezone1 Sun. ON: hour | 230 | 40231 | 1 | 03 | INT | 0-23
| Timezone1 Sun. ON: minute | 231 | 40232 | 1 | 03 | INT | 0-59
| Timezone1 Mon. OFF: hour | 232 | 40233 | 1 | 03 | INT | 0-23
| Timezone1 Mon. OFF: minute | 233 | 40234 | 1 | 03 | INT | 0-59
| Timezone1 Tue. OFF: hour | 234 | 40235 | 1 | 03 | INT | 0-23
| Timezone1 Tue. OFF: minute | 235 | 40236 | 1 | 03 | INT | 0-59
| Timezone1 Wed. OFF: hour | 236 | 40237 | 1 | 03 | INT | 0-23
| Timezone1 Wed. OFF: minute | 237 | 40238 | 1 | 03 | INT | 0-59
| Timezone1 Thu. OFF: hour | 238 | 40239 | 1 | 03 | INT | 0-23
| Timezone1 Thu. OFF: minute | 239 | 40240 | 1 | 03 | INT | 0-59
| Timezone1 Fri. OFF: hour | 240 | 40241 | 1 | 03 | INT | 0-23
| Timezone1 Fri. OFF: minute | 241 | 40242 | 1 | 03 | INT | 0-59
| Timezone1 Sat. OFF: hour | 242 | 40243 | 1 | 03 | INT | 0-23
| Timezone1 Sat. OFF: minute | 243 | 40244 | 1 | 03 | INT | 0-59
| Timezone1 Sun. OFF: hour | 244 | 40245 | 1 | 03 | INT | 0-23
| Timezone1 Sun. OFF: minute | 245 | 40246 | 1 | 03 | INT | 0-59
| Timezone2 Mon. ON: hour | 432 | 40433 | 1 | 03 | INT | 0-23
| Timezone2 Mon. ON: minute | 433 | 40434 | 1 | 03 | INT | 0-59
| Timezone2 Tue. ON: hour | 434 | 40435 | 1 | 03 | INT | 0-23
| Timezone2 Tue. ON: minute | 435 | 40436 | 1 | 03 | INT | 0-59
| Timezone2 Wed. ON: hour | 436 | 40437 | 1 | 03 | INT | 0-23
| Timezone2 Wed. ON: minute | 437 | 40438 | 1 | 03 | INT | 0-59
| Timezone2 Thu. ON: hour | 438 | 40439 | 1 | 03 | INT | 0-23
| Timezone2 Thu. ON: minute | 439 | 40440 | 1 | 03 | INT | 0-59
| Timezone2 Fri. ON: hour | 440 | 40441 | 1 | 03 | INT | 0-23
| Timezone2 Fri. ON: minute | 441 | 40442 | 1 | 03 | INT | 0-59
| Timezone2 Sat. ON: hour | 442 | 40443 | 1 | 03 | INT | 0-23
| Timezone2 Sat. ON: minute | 443 | 40444 | 1 | 03 | INT | 0-59
| Timezone2 Sun. ON: hour | 444 | 40445 | 1 | 03 | INT | 0-23
| Timezone2 Sun. ON: minute | 445 | 40446 | 1 | 03 | INT | 0-59
| Timezone2 Mon. OFF: hour | 446 | 40447 | 1 | 03 | INT | 0-23
| Timezone2 Mon. OFF: minute | 447 | 40448 | 1 | 03 | INT | 0-59
| Timezone2 Tue. OFF: hour | 448 | 40449 | 1 | 03 | INT | 0-23
| Timezone2 Tue. OFF: minute | 449 | 40450 | 1 | 03 | INT | 0-59
| Timezone2 Wed. OFF: hour | 450 | 40451 | 1 | 03 | INT | 0-23
| Timezone2 Wed. OFF: minute | 451 | 40452 | 1 | 03 | INT | 0-59
| Timezone2 Thu. OFF: hour | 452 | 40453 | 1 | 03 | INT | 0-23
| Timezone2 Thu. OFF: minute | 453 | 40454 | 1 | 03 | INT | 0-59
| Timezone2 Fri. OFF: hour | 454 | 40455 | 1 | 03 | INT | 0-23
| Timezone2 Fri. OFF: minute | 455 | 40456 | 1 | 03 | INT | 0-59
| Timezone2 Sat. OFF: hour | 456 | 40457 | 1 | 03 | INT | 0-23
| Timezone2 Sat. OFF: minute | 457 | 40458 | 1 | 03 | INT | 0-59
| Timezone2 Sun. OFF: hour | 458 | 40459 | 1 | 03 | INT | 0-23
| Timezone2 Sun. OFF: minute | 459 | 40460 | 1 | 03 | INT | 0-59
time zone | TimezoneMng.TempHr1 | 246 | 40247 | 1 | 03 | INT | 0-23
| TimezoneMng.TempMin1 | 247 | 40248 | 1 | 03 | INT | 0-59
| TimezoneMng.S_Set_Temp1 | 248 | 40249 | 1 | 03 | REAL | -99.0~99.0
| TimezoneMng.W_Set_Temp1 | 249 | 40250 | 1 | 03 | REAL | -99.0~99.0
| TimezoneMng.TempHr2 | 250 | 40251 | 1 | 03 | INT | 0-95
| TimezoneMng.TempMin2 | 251 | 40252 | 1 | 03 | INT | 0-131
| TimezoneMng.S_Set_Temp2 | 252 | 40253 | 1 | 03 | REAL | -99.0~99.0
| TimezoneMng.W_Set_Temp2 | 253 | 40254 | 1 | 03 | REAL | -99.0~99.0
| TimezoneMng.TempHr3 | 254 | 40255 | 1 | 03 | INT | 0-167
| TimezoneMng.TempMin3 | 255 | 40256 | 1 | 03 | INT | 0-203
| TimezoneMng.S_Set_Temp3 | 256 | 40257 | 1 | 03 | REAL | -99.0~99.0
| TimezoneMng.W_Set_Temp3 | 257 | 40258 | 1 | 03 | REAL | -99.0~99.0
| TimezoneMng.TempHr4 | 258 | 40259 | 1 | 03 | INT | 0-239
| TimezoneMng.TempMin4 | 259 | 40260 | 1 | 03 | INT | 0-275
| TimezoneMng.S_Set_Temp4 | 260 | 40261 | 1 | 03 | REAL | -99.0~99.0
| TimezoneMng.W_Set_Temp4 | 261 | 40262 | 1 | 03 | REAL | -99.0~99.0
Error code | Too many mem writings | 13 | 10014 | 1 | 02 | BOOL | AL001
| Retain mem write error | 14 | 10015 | 1 | 02 | BOOL | AL002
| Inlet probe error | 15 | 10016 | 1 | 02 | BOOL | AL003
| Outlet probe error | 16 | 10017 | 1 | 02 | BOOL | AL004
| Ambient probe error | 17 | 10018 | 1 | 02 | BOOL | AL005
| Condenser coil temp | 18 | 10019 | 1 | 02 | BOOL | AL006
| Water flow switch | 19 | 10020 | 1 | 02 | BOOL | AL007
| Phase sequ.prot.alarm | 20 | 10021 | 1 | 02 | BOOL | AL008
| Unit work hour warning | 21 | 10022 | 1 | 02 | BOOL | AL009
| Pump work hour warning | 22 | 10023 | 1 | 02 | BOOL | AL010
| Comp.work hour warning | 23 | 10024 | 1 | 02 | BOOL | AL011
| Cond.fan work hourWarn | 24 | 10025 | 1 | 02 | BOOL | AL012
| Low superheat - Vlv.A | 25 | 10026 | 1 | 02 | BOOL | AL013
| Low superheat - Vlv.B | 26 | 10027 | 1 | 02 | BOOL | AL014
| LOP - Vlv.A | 27 | 10028 | 1 | 02 | BOOL | AL015
| LOP - Vlv.B | 28 | 10029 | 1 | 02 | BOOL | AL016
| MOP - Vlv.A | 29 | 10030 | 1 | 02 | BOOL | AL017
| MOP - Vlv.B | 30 | 10031 | 1 | 02 | BOOL | AL018
| Motor error - Vlv.A | 31 | 10032 | 1 | 02 | BOOL | AL019
| Motor error - Vlv.B | 32 | 10033 | 1 | 02 | BOOL | AL020
| Low suct.temp. - Vlv.A | 33 | 10034 | 1 | 02 | BOOL | AL021
| Low suct.temp. - Vlv.B | 34 | 10035 | 1 | 02 | BOOL | AL022
| High condens.temp.EVD | 35 | 10036 | 1 | 02 | BOOL | AL023
| Probe S1 error EVD | 36 | 10037 | 1 | 02 | BOOL | AL024
| Probe S2 error EVD | 37 | 10038 | 1 | 02 | BOOL | AL025
| Probe S3 error EVD | 38 | 10039 | 1 | 02 | BOOL | AL026
| Probe S4 error EVD | 39 | 10040 | 1 | 02 | BOOL | AL027
| Battery discharge EVD | 40 | 10041 | 1 | 02 | BOOL | AL028
| EEPROM alarm EVD | 41 | 10042 | 1 | 02 | BOOL | AL029
| Incomplete closing EVD | 42 | 10043 | 1 | 02 | BOOL | AL030
| Emergency closing EVD | 43 | 10044 | 1 | 02 | BOOL | AL031
| FW not compatible EVD | 44 | 10045 | 1 | 02 | BOOL | AL032
| Config. error EVD | 45 | 10046 | 1 | 02 | BOOL | AL033
| EVD Driver offline | 46 | 10047 | 1 | 02 | BOOL | AL034
| BLDC-alarm:High startup DeltaP | 47 | 10048 | 1 | 02 | BOOL | AL035
| BLDC-alarm:Compressor shut off | 48 | 10049 | 1 | 02 | BOOL | AL036
| BLDC-alarm:Out of Envelope | 49 | 10050 | 1 | 02 | BOOL | AL037
| BLDC-alarm:Starting fail wait | 50 | 10051 | 1 | 02 | BOOL | AL038
| BLDC-alarm:Starting fail exceeded | 51 | 10052 | 1 | 02 | BOOL | AL039
| BLDC-alarm:Low delta pressure | 52 | 10053 | 1 | 02 | BOOL | AL040
| BLDC-alarm:High discarge gas temp | 53 | 10054 | 1 | 02 | BOOL | AL041
| Envelope-alarm:High compressor ratio | 54 | 10055 | 1 | 02 | BOOL | AL042
| Envelope-alarm:High discharge press. | 55 | 10056 | 1 | 02 | BOOL | AL043
| Envelope-alarm:High current | 56 | 10057 | 1 | 02 | BOOL | AL044
| Envelope-alarm:High suction pressure | 57 | 10058 | 1 | 02 | BOOL | AL045
| Envelope-alarm:Low compressor ratio | 58 | 10059 | 1 | 02 | BOOL | AL046
| Envelope-alarm:Low pressure diff. | 59 | 10060 | 1 | 02 | BOOL | AL047
| Envelope-alarm:Low discharge pressure | 60 | 10061 | 1 | 02 | BOOL | AL048
| Envelope-alarm:Low suction pressure | 61 | 10062 | 1 | 02 | BOOL | AL049
| Envelope-alarm:High discharge temp. | 62 | 10063 | 1 | 02 | BOOL | AL050
| Power+ alarm:01-Overcurrent | 63 | 10064 | 1 | 02 | BOOL | AL051
| Power+ alarm:02-Motor overload | 64 | 10065 | 1 | 02 | BOOL | AL052
| Power+ alarm:03-DCbus overvoltage | 65 | 10066 | 1 | 02 | BOOL | AL053
| Power+ alarm:04-DCbus undervoltage | 66 | 10067 | 1 | 02 | BOOL | AL054
| Power+ alarm:05-Drive overtemp. | 67 | 10068 | 1 | 02 | BOOL | AL055
| Power+ alarm:06-Drive undertemp. | 68 | 10069 | 1 | 02 | BOOL | AL056
| Power+ alarm:07-Overcurrent HW | 69 | 10070 | 1 | 02 | BOOL | AL057
| Power+ alarm:08-Motor overtemp. | 70 | 10071 | 1 | 02 | BOOL | AL058
| Power+ alarm:09-IGBT module error | 71 | 10072 | 1 | 02 | BOOL | AL059
| Power+ alarm:10-CPU error | 72 | 10073 | 1 | 02 | BOOL | AL060
| Power+ alarm:11-Parameter default | 73 | 10074 | 1 | 02 | BOOL | AL061
| Power+ alarm:12-DCbus ripple | 74 | 10075 | 1 | 02 | BOOL | AL062
| Power+ alarm:13-Data comm. Fault | 75 | 10076 | 1 | 02 | BOOL | AL063
| Power+ alarm:14-Thermistor fault | 76 | 10077 | 1 | 02 | BOOL | AL064
| Power+ alarm:15-Autotuning fault | 77 | 10078 | 1 | 02 | BOOL | AL065
| Power+ alarm:16-Drive disabled | 78 | 10079 | 1 | 02 | BOOL | AL066
| Power+ alarm:17-Motor phase fault | 79 | 10080 | 1 | 02 | BOOL | AL067
| Power+ alarm:18-Internal fan fault | 80 | 10081 | 1 | 02 | BOOL | AL068
| Power+ alarm:19-Speed fault | 81 | 10082 | 1 | 02 | BOOL | AL069
| Power+ alarm:20-PFC module error | 82 | 10083 | 1 | 02 | BOOL | AL070
| Power+ alarm:21-PFC overvoltage | 83 | 10084 | 1 | 02 | BOOL | AL071
| Power+ alarm:22-PFC undervoltage | 84 | 10085 | 1 | 02 | BOOL | AL072
| Power+ alarm:23-STO DetectionError | 85 | 10086 | 1 | 02 | BOOL | AL073
| Power+ alarm:24-STO DetectionError | 86 | 10087 | 1 | 02 | BOOL | AL074
| Power+ alarm:25-Ground fault | 87 | 10088 | 1 | 02 | BOOL | AL075
| Power+ alarm:26-Internal error 1 | 88 | 10089 | 1 | 02 | BOOL | AL076
| Power+ alarm:27-Internal error 2 | 89 | 10090 | 1 | 02 | BOOL | AL077
| Power+ alarm:28-Drive overload | 90 | 10091 | 1 | 02 | BOOL | AL078
| Power+ alarm:29-uC safety fault | 91 | 10092 | 1 | 02 | BOOL | AL079
| Power+ alarm:98-Unexpected restart | 92 | 10093 | 1 | 02 | BOOL | AL080
| Power+ alarm:99-Unexpected stop | 93 | 10094 | 1 | 02 | BOOL | AL081
| Power+ safety alarm:01-Current meas.fault | 94 | 10095 | 1 | 02 | BOOL | AL082
| Power+ safety alarm:02-Current unbalanced | 95 | 10096 | 1 | 02 | BOOL | AL083
| Power+ safety alarm:03-Over current | 96 | 10097 | 1 | 02 | BOOL | AL084
| Power+ safety alarm:04-STO alarm | 97 | 10098 | 1 | 02 | BOOL | AL085
| Power+ safety alarm:05-STO hardware alarm | 98 | 10099 | 1 | 02 | BOOL | AL086
| Power+ safety alarm:06-PowerSupply missing | 99 | 10100 | 1 | 02 | BOOL | AL087
| Power+ safety alarm:07-HW fault cmd.buffer | 100 | 10101 | 1 | 02 | BOOL | AL088
| Power+ safety alarm:08-HW fault heater c. | 101 | 10102 | 1 | 02 | BOOL | AL089
| Power+ safety alarm:09-Data comm. Fault | 102 | 10103 | 1 | 02 | BOOL | AL090
| Power+ safety alarm:10-Compr. stall detect | 103 | 10104 | 1 | 02 | BOOL | AL091
| Power+ safety alarm:11-DCbus over current | 104 | 10105 | 1 | 02 | BOOL | AL092
| Power+ safety alarm:12-HWF DCbus current | 105 | 10106 | 1 | 02 | BOOL | AL093
| Power+ safety alarm:13-DCbus voltage | 106 | 10107 | 1 | 02 | BOOL | AL094
| Power+ safety alarm:14-HWF DCbus voltage | 107 | 10108 | 1 | 02 | BOOL | AL095
| Power+ safety alarm:15-Input voltage | 108 | 10109 | 1 | 02 | BOOL | AL096
| Power+ safety alarm:16-HWF input voltage | 109 | 10110 | 1 | 02 | BOOL | AL097
| Power+ safety alarm:17-DCbus power alarm | 110 | 10111 | 1 | 02 | BOOL | AL098
| Power+ safety alarm:18-HWF power mismatch | 111 | 10112 | 1 | 02 | BOOL | AL099
| Power+ safety alarm:19-NTC over temp. | 112 | 10113 | 1 | 02 | BOOL | AL100
| Power+ safety alarm:20-NTC under temp. | 113 | 10114 | 1 | 02 | BOOL | AL101
| Power+ safety alarm:21-NTC fault | 114 | 10115 | 1 | 02 | BOOL | AL102
| Power+ safety alarm:22-HWF sync fault | 115 | 10116 | 1 | 02 | BOOL | AL103
| Power+ safety alarm:23-Invalid parameter | 116 | 10117 | 1 | 02 | BOOL | AL104
| Power+ safety alarm:24-FW fault | 117 | 10118 | 1 | 02 | BOOL | AL105
| Power+ safety alarm:25-HW fault | 118 | 10119 | 1 | 02 | BOOL | AL106
| Power+ safety alarm:26-reseved | 119 | 10120 | 1 | 02 | BOOL | AL107
| Power+ safety alarm:27-reseved | 120 | 10121 | 1 | 02 | BOOL | AL108
| Power+ safety alarm:28-reseved | 121 | 10122 | 1 | 02 | BOOL | AL109
| Power+ safety alarm:29-reseved | 122 | 10123 | 1 | 02 | BOOL | AL110
| Power+ safety alarm:30-reseved | 123 | 10124 | 1 | 02 | BOOL | AL111
| Power+ safety alarm:31-reseved | 124 | 10125 | 1 | 02 | BOOL | AL112
| Power+ safety alarm:32-reseved | 125 | 10126 | 1 | 02 | BOOL | AL113
| Power+ alarm:Power+ offline | 126 | 10127 | 1 | 02 | BOOL | AL114
| EEV alarm:Low superheat | 127 | 10128 | 1 | 02 | BOOL | AL115
| EEV alarm:LOP | 128 | 10129 | 1 | 02 | BOOL | AL116
| EEV alarm:MOP | 129 | 10130 | 1 | 02 | BOOL | AL117
| EEV alarm:High condens.temp. | 130 | 10131 | 1 | 02 | BOOL | AL118
| EEV alarm:Low suction temp. | 131 | 10132 | 1 | 02 | BOOL | AL119
| EEV alarm:Motor error | 132 | 10133 | 1 | 02 | BOOL | AL120
| EEV alarm:Self Tuning | 133 | 10134 | 1 | 02 | BOOL | AL121
| EEV alarm:Emergency closing | 134 | 10135 | 1 | 02 | BOOL | AL122
| EEV alarm:Temperature delta | 135 | 10136 | 1 | 02 | BOOL | AL123
| EEV alarm:Pressure delta | 136 | 10137 | 1 | 02 | BOOL | AL124
| EEV alarm:Param.range error | 137 | 10138 | 1 | 02 | BOOL | AL125
| EEV alarm:ServicePosit% err | 138 | 10139 | 1 | 02 | BOOL | AL126
| EEV alarm:ValveID pin error | 139 | 10140 | 1 | 02 | BOOL | AL127
| Low press alarm | 140 | 10141 | 1 | 02 | BOOL | AL128
| High press alarm | 141 | 10142 | 1 | 02 | BOOL | AL129
| Disc.temp.probe error | 142 | 10143 | 1 | 02 | BOOL | AL130
| Suct.temp.probe error | 143 | 10144 | 1 | 02 | BOOL | AL131
| Disc.press.probe error | 144 | 10145 | 1 | 02 | BOOL | AL132
| Suct.press.probe error | 145 | 10146 | 1 | 02 | BOOL | AL133
| Tank temp.probe error | 146 | 10147 | 1 | 02 | BOOL | AL134
| EVI SuctT.probe error | 147 | 10148 | 1 | 02 | BOOL | AL135
| EVI SuctP.probe error | 148 | 10149 | 1 | 02 | BOOL | AL136
| Flow switch alarm | 149 | 10150 | 1 | 02 | BOOL | AL137
| High temp. alarm | 150 | 10151 | 1 | 02 | BOOL | AL138
| Low temp. alarm | 151 | 10152 | 1 | 02 | BOOL | AL139
| Temp.delta alarm | 152 | 10153 | 1 | 02 | BOOL | AL140
| EVI alarm:Param.range error | 153 | 10154 | 1 | 02 | BOOL | AL141
| EVI alarm:Low superheat | 154 | 10155 | 1 | 02 | BOOL | AL142
| EVI alarm:LOP | 155 | 10156 | 1 | 02 | BOOL | AL143
| EVI alarm:MOP | 156 | 10157 | 1 | 02 | BOOL | AL144
| EVI alarm:High condens.temp. | 157 | 10158 | 1 | 02 | BOOL | AL145
| EVI alarm:Low suction temp. | 158 | 10159 | 1 | 02 | BOOL | AL146
| EVI alarm:Motor error | 159 | 10160 | 1 | 02 | BOOL | AL147
| EVI alarm:Self Tuning | 160 | 10161 | 1 | 02 | BOOL | AL148
| EVI alarm:Emergency closing | 161 | 10162 | 1 | 02 | BOOL | AL149
| EVI alarm:ServicePosit% err | 162 | 10163 | 1 | 02 | BOOL | AL150
| EVI alarm:ValveID pin error | 163 | 10164 | 1 | 02 | BOOL | AL151
| Supply power error | 164 | 10165 | 1 | 02 | BOOL | AL152
| Fan1 fault | 165 | 10166 | 1 | 02 | BOOL | AL153
| Fan2 fault | 166 | 10167 | 1 | 02 | BOOL | AL154
| Fans Offline | 167 | 10168 | 1 | 02 | BOOL | AL155
| Slave1 Offline | 168 | 10169 | 1 | 02 | BOOL | AL165
| Master Offline | 169 | 10170 | 1 | 02 | BOOL | AL166
| Slave2 Offline | 170 | 10171 | 1 | 02 | BOOL | AL167
| Slave3 Offline | 171 | 10172 | 1 | 02 | BOOL | AL168
| Slave4 Offline | 172 | 10173 | 1 | 02 | BOOL | AL169
| Slave5 Offline | 173 | 10174 | 1 | 02 | BOOL | AL170
| Slave6 Offline | 174 | 10175 | 1 | 02 | BOOL | AL171
| Slave7 Offline | 175 | 10176 | 1 | 02 | BOOL | AL172
| Slave8 Offline | 176 | 10177 | 1 | 02 | BOOL | AL173
| Slave9 Offline | 177 | 10178 | 1 | 02 | BOOL | AL174
| Al_Offline_ElectricMeter.Active | 188 | 10189 | 1 | 02 | BOOL | AL177
Anti-legionella | Anti-legionella funtion | 109 | 00110 | 1 | 01 | Coil | 0：disable 1：enable
| Anti-legionella temp.setp. | 471 | 40472 | 2 | 03 | real | 30-70
| Weekday of running antileg. | 473 | 40474 | 1 | 03 | UNIT | 1~7
| Timeband of runnig antileg.- hours (start) | 474 | 40475 | 1 | 03 | UNIT | 0-23
| Timeband of runnig antileg. - minutes (start) | 475 | 40476 | 1 | 03 | UNIT | 0-59
| Timeband of runnig antileg. - hours (end) | 476 | 40477 | 1 | 03 | UNIT | 0-23
| Timeband of runnig antileg. - minutes (end) | 477 | 40478 | 1 | 03 | UNIT | 0-59
| Manual defrosting | 105 | 00106 | 1 | 01 | Coil | 0：disable 1：enable
SG ready | En_SG_Function | 63 | 00064 | 1 | 01 | BOOL | 0：disable 2：enable
| En_SG_HotwaterHeater | 64 | 00065 | 1 | 01 | BOOL | 0：disable 3：enable
| Hotwater Heater_In_Pipe or water tank | 65 | 00066 | 1 | 01 | BOOL | 0：water tank 1：PIPE
| SG_Mode | 355 | 40356 | 1 | 03 | int | 0=NORMAL，1=SG-，2=SG+，3=SG++
| SG_Mode Change_HoldTime | 356 | 40357 | 1 | 03 | int | 0~600秒
| SG_Mode_W_Tank SetP | 357 | 40358 | 1 | 03 | real | 56.0~70.0℃
| SG_CoolSetP_Diff_1 | 358 | 40359 | 1 | 03 | real | 0.0~10.0℃
| SG_HeatSetP_Diff_1 | 359 | 40360 | 1 | 03 | real | 0.0~10.0℃
| SG_W_TankSetP_Diff_1 | 360 | 40361 | 1 | 03 | real | 设0.0~10.0℃
| SG_CoolSetP_Diff_2 | 361 | 40362 | 1 | 03 | real | 0.0~10.0℃
| SG_HeatSetP_Diff_2 | 362 | 40363 | 1 | 03 | real | 0.0~10.0℃
| SG_W_TankSetP_Diff_2 | 363 | 40364 | 1 | 03 | real | 0.0~10.0℃
Electric Meter | Enable_ElectricMeter | 67 | 00068 | 1 | 01 | BOOL | 0：disable 1：enable
| ElectricMeter_Reset | 68 | 00069 | 1 | 01 | BOOL
| PhaseVoltage_A | 376 | 40377 | 1 | 03 | real | V
| PhaseVoltage_B | 377 | 40378 | 1 | 03 | real | V
| PhaseVoltage_C | 378 | 40379 | 1 | 03 | real | V
| PhaseCurrent_A | 379 | 40380 | 1 | 03 | real | A
| PhaseCurrent_B | 380 | 40381 | 1 | 03 | real | A
| PhaseCurrent_C | 381 | 40382 | 1 | 03 | real | A
| Power_W | 382 | 40383 | 2 | 03 | real | W
| Total power consumption | 384 | 40385 | 2 | 03 | real | Kw.h
| Record_PowerConsumption[1] | 401 | 40402 | 2 | 03 | REAL | Kw.h
| Record_PowerConsumption[2] | 403 | 40404 | 2 | 03 | REAL | Kw.h
| Record_PowerConsumption[3] | 405 | 40406 | 2 | 03 | REAL | Kw.h
| Record_PowerConsumption[4] | 407 | 40408 | 2 | 03 | REAL | Kw.h
| Record_PowerConsumption[5] | 409 | 40410 | 2 | 03 | REAL | Kw.h
| Record_PowerConsumption[6] | 411 | 40412 | 2 | 03 | REAL | Kw.h
| Record_PowerConsumption[7] | 413 | 40414 | 2 | 03 | REAL | Kw.h